## Template Guide
EMIS Field Evaluation Reporting Summary: Template Guide
About this Template
This template is designed to facilitate reporting on results from EMIS implementations using the approach described in LBNL's Energy Management and Information System Field Evaluation Protocol. The protocol provides a standardized approach to assessing the energy and non-energy benefits from use of EMIS. The template enables reporting on the required and optional metrics identified in the protocol. Template tips: ◆︎ Required fields are identified with an orange background and optional fields with a yellow background (see Legend below). ◆︎ The template has six (6) reporting sections with a separate tab for each section. Use the workbook tabs to navigate between sections. ◆︎ Use the template to report results on individual buildings or campuses. Use multiple templates to report results from multiple buildings. For portfolio or program-level reporting, contact emis@lbl.gov. After completing all sections, save the template and email it as an attachment to emis@lbl.gov. If you have questions or comments on the protocol or the use of this template, send email to emis@lbl.gov.
Quick Links |  | Legend
EMIS Field Evaluation Protocol |  | Orange: Required Fields
Protocol Fact Sheet |  | Yellow: Optional Fields
Contact LBNL EMIS Team |  | Gray: Tips - do not edit
Contact details for person completing the template:
Name: | Eliot Crowe
Organization/Company: | Lawrence Berkeley National Laboratory
Email: | ecrowe@lbl.gov
* Submit your completed template to emis@lbl.gov
Refer to the Energy Management and Information System Field Evaluation Protocol for data and metric definitions and other guidance on EMIS evaluation and reporting.

## Building
EMIS Field Evaluation Reporting Summary: Building Information
Building Description
Building Name: | Large Office Building
Building Location - City: | San Diego
Building Location - State: | CA
Building Size (square feet): | 144000
Building Location - Climate Zone: | [enter County, Zip Code, or Climate Zone]
Building Type: | Office
For Other Building Type (describe):
Occupancy Schedule
Monday |  | from | 5:00 | to | 18:00
Tuesday |  | from | 5:00 | to | 18:00
Wednesday |  | from | 5:00 | to | 18:00
Thursday |  | from | 5:00 | to | 18:00
Friday |  | from | 5:00 | to | 18:00
Saturday |  | from | 8:00 | to | 13:00
Sunday |  | from | 0:00 | to | 0:00
Building Automation System
Make: | Johnson Controls
Model: | Metasys
Building Systems & Equipment Covered by EMIS
HVAC |  | Metering
Central cooling plant |  | Lighting
Central heating plant |  | Plug Loads
Air handling unit
Rooftop unit
Terminal units
Chiller
Boiler
Cooling tower
Pump
Fan
Other systems (describe):

## EMIS Data Points
EMIS Field Evaluation Reporting Summary: Technology Information - Data Points
EMIS System Description
System Name: | Predictive HVAC Control Enhancement Software (not named)
Vendor Name: | Not specified
Data Points Integrated into EMIS (mark all those that apply):
Interval energy & power meter data
Whole building electricity meter |  | Electric submeter - for end uses
Whole building gas meter |  | Chilled water BTU meter
Whole building water meter |  | Hot water BTU meter
Electric submeter - for tenants |  | Steammass flow meter
Other interval & power meter data (describe): | Report specifies "any power metering points" in list of data collected, but does not give specifics
HVAC system trend data
Central cooling plant trend data |  | Rooftop unit trend data
Central heating plant trend data |  | Terminal units & thermostat trend data
Air handling unit trend data
Other HVAC system trend data (describe):
Sensor data
Temperature sensor data |  | Occupancy sensor data
Humidity sensor data |  | Carbon dioxide sensor data
Other sensor data (describe):
Lighting control system trend data |  | Plug load control system trend data
Other system trend data (describe):

## EMIS Functionality
EMIS Field Evaluation Reporting Summary: Technology Information - Functionality
EMIS Functionality & Capabilities (mark all those that apply):
Energy Information System
Energy consumption (costs) visualization
EIS performance indicator (KPI) tracking
Energy performance analysis
Demand management
Measurement and verification
Energy reporting and data export
Other EIS capabilities (describe):
Fault detection and diagnostics
Operational data visualization
FDD key performance indicator (KPI) tracking
Fault prioritization
Fault reporting and data export
Other FDD capabilities (describe):
Automated system optimization
System/equipment on/off schedule
Central cooling plant chilled water leaving temperature setpoint
Central cooling plant cooling tower leaving temperature setpoint
Central cooling plant hydronic differential pressure setpoint
Central cooling plant chiller/pump/cooling tower staging
Central heating plant chilled water leaving temperature setpoint
Central heating plant hydronic differential pressure setpoint
Central heating plant boiler/pump staging
AHU/RTU supply air temperature setpoint
AHU/RTU supply air static pressure setpoint
Space heating and cooling setpoints
Other ASO capabilities (describe):

## Savings & Costs
EMIS Field Evaluation Reporting Summary: Energy and Utility Savings & Costs
Time Periods
Baseline Period | Start Date | 2013-05-01 | End Date | 2014-10-01
Reporting Period | Start Date | 2014-11-01 | End Date | 2015-08-03
Savings Calculation Approach
IPMVP Options (select) | C-Whole Facility
Other (describe)
Energy and Utility Cost Savings |  | Value (enter) | Units
| Annual energy savings (kBtu) | 284231 | kBtu
| Annual energy savings (%) | 10.7 | %
| Annual energy intensity savings (kBtu / sqft) |  | kBtu/sqft
| Annual energy cost savings | 10826 | $/year
| Monthly non-coincident peak demand reduction |  | kW
| Monthly coincident peak demand reduction | 10 | kW
| Demand response load reduction | 14 | kW
EMIS Technology Costs
|  | Base Cost (install & commission) |  | Recurring Cost (annual)
EMIS technology software costs |  | 8500 | $ | 3700 | $/year
| EMIS technology hardware costs |  | $ |  | $/year
| EMIS 3rd party services costs | 8500 | $ | 7000 | $/year
| In-house labor cost estimate |  | $ |  | $/year
Cost Effectiveness
Simple Payback |  | 6.5 | years
| Net present value |  | $
Savings-to-investment ratio

## Measures
EMIS Field Evaluation Reporting Summary: Capability to Enable Energy Efficiency
Measures enabled or resolved through EMIS (mark all those that apply):
Category | Operational Improvement Measures | Select all measures that apply (Required) | Enter number of actions (Optional)
Scheduling Equipment Loads | Improve scheduling for HVAC
Improve scheduling for lighting
Improve scheduling for plug loads
Economizer /Outside Air Loads | Improve economizer operation/use
Reduce over-ventilation
Control Problems | Reduce simultaneous heating and cooling
Tune control loops to avoid hunting
Optimize equipment staging
Zone rebalancing
Controls: Setpoint Changes | Adjustment of heating/cooling and occupied/unoccupied space temperature setpoints
Reduction of VAV box minimum setpoint
Duct static pressure setpoint change
Hydronic differential pressure setpoint change
Preheat temperature setpoint change
Controls: Reset Schedule Addition or Modification | Supply air temperature reset
Duct static pressure reset
Chilled water supply temperature reset
Hot water supply temperature reset or hot water plant lockout
Condenser water supply temperature reset
Equipment Efficiency Improvements | Add or optimize variable frequency drives (VFDs)
Pump discharge throttled or over-pumping and low delta T
Occupant Behavior Modification | Routinely share energy information or guidance on proper use of equipment with occupants through EMIS
Hold an energy savings challenge using EMIS data
Retrofits | Lighting upgrade or improve lighting controls: replace lighting fixtures with more efficient fixtures, add lighting control system.
High efficiency HVAC equipment: airside: replace airside HVAC equipment with more efficient equipment.
High efficiency HVAC equipment: waterside: replace waterside HVAC equipment with more efficient equipment.
Other operational improvement measures (describe any additional measures)

## Operations
EMIS Field Evaluation Reporting Summary: Operational capabilities (optional reporting)
Installation & Commissioning Process Effort
Elapsed time to complete installation | [enter #] | weeks
Elapsed time to complete commissioning | 10 | weeks
Activities during installation phase (describe)
Develop generic model of building's HVAC operations, and then install technology which continuously improves the quality/accuracy of that predictive model over a 4-6 week period
Activities during commissioning phase (describe)
Once the model has completed the learning phase, the predictive controls are slowly transitioned into effect over a 4-6 week period. Based on the predictive model, the system optimizes air-side HVAC schedules and set points to achieve the most efficient operating point. The most efficient operating point is defined by minimizing overall energy cost.
Support needed from on-site staff during installation phase (describe)
Support needed from on-site staff during commissioning phase (describe)
Best Practices (describe)
Lessons Learned (describe)
Accuracy of issues/opportunities identified by FDD (describe)
Occupant comfort (describe)
As demonstrated in the M&V results, the space temperature varied slightly after the new software was installed, but not significantly enough to affect occupant comfort. No increase in occupant complaints
Operation and maintenance (describe)
The building engineer at the location studied in this project stated during a telephone interview that the software provider contacted him on numerous occasions to inform him when supply air or return air temperatures exceeded their normal operating conditions. These remote observations allowed the building engineer to quickly assess and fix issues with his HVAC systems. Additionally, the building engineer noted that the provider was very responsive when he called them to report any hot calls in the building.

## Lookups (hide) (hidden)
[Hour] | [CBECS Building Type] | [IPMVP Option]
0:00 | Education | A-Partially Measured Retrofit Isolation
1:00 | Food Sales | B-Retrofit Isolation
2:00 | Food Service | C-Whole Facility
3:00 | Health Care (Inpatient) | D-Calibrated Simulation
4:00 | Health Care (Outpatient) | Other (describe below)
5:00 | Lodging
6:00 | Mercantile (Retail - not Mall)
7:00 | Mercantile (Enclosed or Strip Mall)
8:00 | Office
9:00 | Public Assembly
10:00 | Public Order and Safety
11:00 | Religious Worship
12:00 | Service
13:00 | Warehouse and Storage
14:00 | Other
15:00
16:00
17:00
18:00
19:00
20:00
21:00
22:00
23:00

## DataExport (hide) (hidden)
Order | Tab | Field Name | Required? | Expected value | Entered | 1-Reqd
1 | 1.Building | Building name | 1-Reqd | Short Text | Large Office Building | 2-Opt
2 | 1.Building | Building location_City | 1-Reqd | Short Text | San Diego | 3-DK
3 | 1.Building | Building location_State | 1-Reqd | Text (list?) | CA
4 | 1.Building | Building location_Climate Zone | 2-Opt | ?? | 144000
5 | 1.Building | Building type | 1-Reqd | Text (list?) | [enter County, Zip Code, or Climate Zone]
6 | 1.Building | Building area | 2-Opt |  | Office
7 | 1.Building | 1. Mon-Occupied Schedule Day | 2-Opt | T/F | TRUE
8 | 1.Building | 1. Mon-Occupied Day Start Time | 2-Opt | Time (0 to 24) | 0.20833
9 | 1.Building | 1. Mon-Occupied Day End Time | 2-Opt | Time (0 to 24) | 0.75
10 | 1.Building | 2. Tue-Occupied Schedule Day | 2-Opt | T/F | TRUE
11 | 1.Building | 2. Tue-Occupied Day Start Time | 2-Opt | Time (0 to 24) | 0.20833
12 | 1.Building | 2. Tue-Occupied Day End Time | 2-Opt | Time (0 to 24) | 0.75
13 | 1.Building | 3. Wed-Occupied Schedule Day | 2-Opt | T/F | TRUE
14 | 1.Building | 3. Wed-Occupied Day Start Time | 2-Opt | Time (0 to 24) | 0.20833
15 | 1.Building | 3. Wed-Occupied Day End Time | 2-Opt | Time (0 to 24) | 0.75
16 | 1.Building | 4. Thu-Occupied Schedule Day | 2-Opt | T/F | TRUE
17 | 1.Building | 4. Thu-Occupied Day Start Time | 2-Opt | Time (0 to 24) | 0.20833
18 | 1.Building | 4. Thu-Occupied Day End Time | 2-Opt | Time (0 to 24) | 0.75
19 | 1.Building | 5. Fri-Occupied Schedule Day | 2-Opt | T/F | TRUE
20 | 1.Building | 5. Fri-Occupied Day Start Time | 2-Opt | Time (0 to 24) | 0.20833
21 | 1.Building | 5. Fri-Occupied Day End Time | 2-Opt | Time (0 to 24) | 0.75
22 | 1.Building | 6. Sat-Occupied Schedule Day | 2-Opt | T/F | TRUE
23 | 1.Building | 6. Sat-Occupied Day Start Time | 2-Opt | Time (0 to 24) | 0.33333
24 | 1.Building | 6. Sat-Occupied Day End Time | 2-Opt | Time (0 to 24) | 0.54167
25 | 1.Building | 7. Sun-Occupied Schedule Day | 2-Opt | T/F | FALSE
26 | 1.Building | 7. Sun-Occupied Day Start Time | 2-Opt | Time (0 to 24) | 0
27 | 1.Building | 7. Sun-Occupied Day End Time | 2-Opt | Time (0 to 24) | 0
28 | 1.Building | Building Automation System_Model | 1-Reqd | Text | Johnson Controls
29 | 1.Building | Building Automation System_Make | 1-Reqd | Text | Metasys
30 | 1.Building | HVAC system | 1-Reqd | Yes/No | TRUE
31 | 1.Building | Central cooling plant | 1-Reqd | Yes/No | FALSE
32 | 1.Building | Central heating plant | 1-Reqd | Yes/No | FALSE
33 | 1.Building | Air handler unit | 1-Reqd | Yes/No | FALSE
34 | 1.Building | Rooftop unit | 1-Reqd | Yes/No | FALSE
35 | 1.Building | Terminal units | 1-Reqd | Yes/No | FALSE
36 | 1.Building | Chiller | 1-Reqd | Yes/No | FALSE
37 | 1.Building | Boiler | 1-Reqd | Yes/No | FALSE
38 | 1.Building | Cooling tower | 1-Reqd | Yes/No | FALSE
39 | 1.Building | Pump | 1-Reqd | Yes/No | FALSE
40 | 1.Building | Fan | 1-Reqd | Yes/No | FALSE
41 | 1.Building | Metering system | 1-Reqd | Yes/No | FALSE
42 | 1.Building | Lighting system | 1-Reqd | Yes/No | FALSE
43 | 1.Building | Plug load system | 1-Reqd | Yes/No | FALSE
44 | 1.Building | Other system, please describe | 1-Reqd | Yes/No | 0
45 | 2.Data | EMIS name | 1-Reqd | Text | Predictive HVAC Control Enhancement Software (not named)
46 | 2.Data | EMIS vendor name | 1-Reqd | Text | Not specified
47 | 2.Data | Interval energy and power meter data | 1-Reqd | Yes/No | FALSE
48 | 2.Data | Whole building electricity meter | 1-Reqd | Yes/No | FALSE
49 | 2.Data | Whole building gas meter | 1-Reqd | Yes/No | FALSE
50 | 2.Data | Whole building water meter | 1-Reqd | Yes/No | FALSE
51 | 2.Data | Electric submeter - for tenants | 1-Reqd | Yes/No | FALSE
52 | 2.Data | Electric submeter - for end uses | 1-Reqd | Yes/No | FALSE
53 | 2.Data | Chilled water BTU meter | 1-Reqd | Yes/No | FALSE
54 | 2.Data | Hot water BTU meter | 1-Reqd | Yes/No | FALSE
55 | 2.Data | Steammass flow meter | 1-Reqd | Yes/No | FALSE
56 | 2.Data | Other energy and power meter data, please describe | 1-Reqd | Text | Report specifies "any power metering points" in list of data collected, but does not give specifics
57 | 2.Data | HVAC system trend data | 1-Reqd | Yes/No | TRUE
58 | 2.Data | Central cooling plant trend data | 1-Reqd | Yes/No | FALSE
59 | 2.Data | Central heating plant trend data | 1-Reqd | Yes/No | FALSE
60 | 2.Data | Air handler unit trend data | 1-Reqd | Yes/No | TRUE
61 | 2.Data | Rooftop unit trend data | 1-Reqd | Yes/No | FALSE
62 | 2.Data | Terminal units and thermostat trend data | 1-Reqd | Yes/No | TRUE
63 | 2.Data | Other HVAC system trend data, please describe | 1-Reqd | Text | 0
64 | 2.Data | IoT sensor data | 1-Reqd | Yes/No | FALSE
65 | 2.Data | IoT temperature sensor data | 1-Reqd | Yes/No | FALSE
66 | 2.Data | IoT humidity sensor data | 1-Reqd | Yes/No | FALSE
67 | 2.Data | IoT occupancy sensor data | 1-Reqd | Yes/No | FALSE
68 | 2.Data | IoT carbon dioxide sensor data | 1-Reqd | Yes/No | FALSE
69 | 2.Data | Other IoT sensor data, please describe | 1-Reqd | Text | 0
70 | 2.Data | Lighting control system trend data | 1-Reqd | Yes/No | FALSE
71 | 2.Data | Plug load control system trend data | 1-Reqd | Yes/No | FALSE
72 | 2.Data | Others system trend data, please describe | 1-Reqd | Text | 0
73 | 3.Function | Energy Information System | 1-Reqd | Yes/No | FALSE
74 | 3.Function | Energy consumption(costs) visualization | 1-Reqd | Yes/No | FALSE
75 | 3.Function | EIS performance indicator (KPI) tracking | 1-Reqd | Yes/No | FALSE
76 | 3.Function | Energy performance analysis | 1-Reqd | Yes/No | FALSE
77 | 3.Function | Demand management | 1-Reqd | Yes/No | FALSE
78 | 3.Function | Measurement and verification | 1-Reqd | Yes/No | FALSE
79 | 3.Function | Energy reporting and data export | 1-Reqd | Yes/No | FALSE
80 | 3.Function | Other EIS capabilities, please describe | 1-Reqd | Text | 0
81 | 3.Function | Fault detection and diagnostics | 1-Reqd | Yes/No | FALSE
82 | 3.Function | Operational data visualization | 1-Reqd | Yes/No | FALSE
83 | 3.Function | FDD key performance indicator (KPI) tracking | 1-Reqd | Yes/No | FALSE
84 | 3.Function | Fault prioritization | 1-Reqd | Yes/No | FALSE
85 | 3.Function | Fault reporting and data export | 1-Reqd | Yes/No | FALSE
86 | 3.Function | Other FDD capabilities, please describe | 1-Reqd | Text | 0
87 | 3.Function | Automated system optimization | 1-Reqd | Yes/No | TRUE
88 | 3.Function | System/equipment on/off schedule | 1-Reqd | Yes/No | TRUE
89 | 3.Function | Central cooling plant chilled water leaving temperature setpoint | 1-Reqd | Yes/No | FALSE
90 | 3.Function | Central cooling plant cooling tower leaving temperature setpoint | 1-Reqd | Yes/No | FALSE
91 | 3.Function | Central cooling plant hydronic differential pressure setpoint | 1-Reqd | Yes/No | FALSE
92 | 3.Function | Central cooling plant chiller/pump/cooling tower staging | 1-Reqd | Yes/No | FALSE
93 | 3.Function | Central heating plant chilled water leaving temperature setpoint | 1-Reqd | Yes/No | FALSE
94 | 3.Function | Central heating plant hydronic differential pressure setpoint | 1-Reqd | Yes/No | FALSE
95 | 3.Function | Central heating plant boiler/pump staging | 1-Reqd | Yes/No | FALSE
96 | 3.Function | AHU/RTU supply air temperature setpoint | 1-Reqd | Yes/No | TRUE
97 | 3.Function | AHU/RTU supply air static pressure setpoint | 1-Reqd | Yes/No | TRUE
98 | 3.Function | Space heating and cooling setpoints | 1-Reqd | Yes/No | TRUE
99 | 3.Function | Other ASO capabilities, please describe | 1-Reqd | Text | 0
100 | 4.Report1 | Baseline period_Start date | 1-Reqd | Date | 2013-05-01
101 | 4.Report1 | Baseline period_End date | 1-Reqd | Date | 2014-10-01
102 | 4.Report1 | Reporting period_Start date | 1-Reqd | Date | 2014-11-01
103 | 4.Report1 | Reporting period_End date | 1-Reqd | Date | 2015-08-03
104 | 4.Report1 | Savings calculation approach (IPMVP option) | 1-Reqd | Lookup | C-Whole Facility
105 | 4.Report1 | Savings calc - other | 2-Opt | Text | 0
106 | 4.Report1 | Annual energy savings_kBtu | 1-Reqd | kBtu | 284231
107 | 4.Report1 | Annual energy savings_Percentage | 1-Reqd | % | 10.7
108 | 4.Report1 | Annual energy savings_Intensity | 1-Reqd | kBtu/sqft
109 | 4.Report1 | Annual energy cost savings | 1-Reqd | $/year | 10826
110 | 4.Report1 | Monthly non-coincident peak demand reduction | 1-Reqd | kW | 0
111 | 4.Report1 | Monthly coincident peak demand reduction | 1-Reqd | kW | 10
112 | 4.Report1 | Demand response load reduction | 1-Reqd | kW | 14
113 | 4.Report1 | Base costs - EMIS software | 1-Reqd | $ | 8500
114 | 4.Report1 | Base costs - EMIS hardware | 1-Reqd | $ | 0
115 | 4.Report1 | Base costs - 3rd party services | 1-Reqd | $ | 8500
116 | 4.Report1 | Base costs - in house labor | 1-Reqd | $ | 0
117 | 4.Report1 | Annual costs - EMIS software | 1-Reqd | $/year | 3700
118 | 4.Report1 | Annual costs - EMIS hardware | 1-Reqd | $/year | 0
119 | 4.Report1 | Annual costs - 3rd party services | 1-Reqd | $/year | 7000
120 | 4.Report1 | Annual costs - in house labor | 1-Reqd | $/year | 0
121 | 4.Report1 | Simple payback | 1-Reqd | years | 6.5
122 | 4.Report1 | Net present value | 2-Opt | $ | 0
123 | 4.Report1 | Savings-to-investment ratio | 2-Opt |  | 0
124 | 5.Report2 | Improve scheduling for HVAC | 1-Reqd | T/F | TRUE
125 | 5.Report2 | Improve scheduling for lighting | 1-Reqd | T/F | FALSE
126 | 5.Report2 | Improve scheduling for plug loads | 1-Reqd | T/F | FALSE
127 | 5.Report2 | Improve economizer operation/use | 1-Reqd | T/F | TRUE
128 | 5.Report2 | Reduce over-ventilation | 1-Reqd | T/F | TRUE
129 | 5.Report2 | Reduce simultaneous heating and cooling | 1-Reqd | T/F | FALSE
130 | 5.Report2 | Tune control loops to avoid hunting | 1-Reqd | T/F | FALSE
131 | 5.Report2 | Optimize equipment staging | 1-Reqd | T/F | FALSE
132 | 5.Report2 | Zone rebalancing | 1-Reqd | T/F | FALSE
133 | 5.Report2 | Adjustment of heating/cooling and occupied/unoccupied space temperature setpoints | 1-Reqd | T/F | TRUE
134 | 5.Report2 | Reduction of VAV box minimum setpoint | 1-Reqd | T/F | FALSE
135 | 5.Report2 | Duct static pressure setpoint change | 1-Reqd | T/F | TRUE
136 | 5.Report2 | Hydronic differential pressure setpoint change | 1-Reqd | T/F | FALSE
137 | 5.Report2 | Preheat temperature setpoint change | 1-Reqd | T/F | FALSE
138 | 5.Report2 | Supply air temperature reset | 1-Reqd | T/F | TRUE
139 | 5.Report2 | Duct static pressure reset | 1-Reqd | T/F | TRUE
140 | 5.Report2 | Chilled water supply temperature reset | 1-Reqd | T/F | FALSE
141 | 5.Report2 | Hot water supply temperature reset or hot water plant lockout | 1-Reqd | T/F | FALSE
142 | 5.Report2 | Condenser water supply temperature reset | 1-Reqd | T/F | FALSE
143 | 5.Report2 | Add or optimize variable frequency drives (VFDs) | 1-Reqd | T/F | TRUE
144 | 5.Report2 | Pump discharge throttled or over-pumping and low delta T | 1-Reqd | T/F | FALSE
145 | 5.Report2 | Routinely share energy information or guidance on proper use of equipment with occupants through EMIS | 1-Reqd | T/F | FALSE
146 | 5.Report2 | Hold an energy savings challenge using EMIS data | 1-Reqd | T/F | FALSE
147 | 5.Report2 | Lighting upgrade or improve lighting controls | 1-Reqd | T/F | FALSE
148 | 5.Report2 | High efficiency HVAC equipment | 1-Reqd | T/F | FALSE
149 | 5.Report2 | High efficiency HVAC equipment | 1-Reqd | T/F | FALSE
150 | 5.Report2 | Improve scheduling for HVAC | 2-Opt | Count | 0
151 | 5.Report2 | Improve scheduling for lighting | 2-Opt | Count | 0
152 | 5.Report2 | Improve scheduling for plug loads | 2-Opt | Count | 0
153 | 5.Report2 | Improve economizer operation/use | 2-Opt | Count | 0
154 | 5.Report2 | Reduce over-ventilation | 2-Opt | Count | 0
155 | 5.Report2 | Reduce simultaneous heating and cooling | 2-Opt | Count | 0
156 | 5.Report2 | Tune control loops to avoid hunting | 2-Opt | Count | 0
157 | 5.Report2 | Optimize equipment staging | 2-Opt | Count | 0
158 | 5.Report2 | Zone rebalancing | 2-Opt | Count | 0
159 | 5.Report2 | Adjustment of heating/cooling and occupied/unoccupied space temperature setpoints | 2-Opt | Count | 0
160 | 5.Report2 | Reduction of VAV box minimum setpoint | 2-Opt | Count | 0
161 | 5.Report2 | Duct static pressure setpoint change | 2-Opt | Count | 0
162 | 5.Report2 | Hydronic differential pressure setpoint change | 2-Opt | Count | 0
163 | 5.Report2 | Preheat temperature setpoint change | 2-Opt | Count | 0
164 | 5.Report2 | Supply air temperature reset | 2-Opt | Count | 0
165 | 5.Report2 | Duct static pressure reset | 2-Opt | Count | 0
166 | 5.Report2 | Chilled water supply temperature reset | 2-Opt | Count | 0
167 | 5.Report2 | Hot water supply temperature reset or hot water plant lockout | 2-Opt | Count | 0
168 | 5.Report2 | Condenser water supply temperature reset | 2-Opt | Count | 0
169 | 5.Report2 | Add or optimize variable frequency drives (VFDs) | 2-Opt | Count | 0
170 | 5.Report2 | Pump discharge throttled or over-pumping and low delta T | 2-Opt | Count | 0
171 | 5.Report2 | Routinely share energy information or guidance on proper use of equipment with occupants through EMIS | 2-Opt | Count | 0
172 | 5.Report2 | Hold an energy savings challenge using EMIS data | 2-Opt | Count | 0
173 | 5.Report2 | Lighting upgrade or improve lighting controls | 2-Opt | Count | 0
174 | 5.Report2 | High efficiency HVAC equipment | 2-Opt | Count | 0
175 | 5.Report2 | High efficiency HVAC equipment | 2-Opt | Count | 0
176 | 5.Report2 | Other measure 1 Desc | 2-Opt | Text | 0
177 | 5.Report2 | Other measure 2 Desc | 2-Opt | Text | 0
178 | 5.Report2 | Other measure 3 Desc | 2-Opt | Text | 0
179 | 5.Report2 | Other measure 4 Desc | 2-Opt | Text | 0
180 | 5.Report2 | Other measure 5 Desc | 2-Opt | Text | 0
181 | 5.Report2 | Other measure 1 Count | 2-Opt | Count | 0
182 | 5.Report2 | Other measure 2 Count | 2-Opt | Count | 0
183 | 5.Report2 | Other measure 3 Count | 2-Opt | Count | 0
184 | 5.Report2 | Other measure 4 Count | 2-Opt | Count | 0
185 | 5.Report2 | Other measure 5 Count | 2-Opt | Count | 0
186 | 6.Report3 | Installation lead time | 2-Opt | # of weeks | [enter #]
187 | 6.Report3 | Commissioning lead time | 2-Opt | # of weeks | 10
188 | 6.Report3 | Activities during the installation phase | 2-Opt | Long Text | Develop generic model of building's HVAC operations, and then install technology which continuously improves the quality/accuracy of that predictive model over a 4-6 week period
189 | 6.Report3 | Activities during the commissioning phase | 2-Opt | Long Text | Once the model has completed the learning phase, the predictive controls are slowly transitioned into effect over a 4-6 week period. Based on the predictive model, the system optimizes air-side HVAC schedules and set points to achieve the most efficient operating point. The most efficient operating point is defined by minimizing overall energy cost.
190 | 6.Report3 | Support needed from the on-site staff during the installation phase | 2-Opt | Long Text | 0
191 | 6.Report3 | Support needed from the on-site staff during the commissioning phase | 2-Opt | Long Text | 0
192 | 6.Report3 | Best practices | 2-Opt | Long Text | 0
193 | 6.Report3 | Lessons learned | 2-Opt | Long Text | 0
194 | 6.Report3 | Accuracy of issues/opportunities identified by the FDD | 2-Opt | Long Text | 0
195 | 6.Report3 | Occupant comfort | 2-Opt | Long Text | As demonstrated in the M&V results, the space temperature varied slightly after the new software was installed, but not significantly enough to affect occupant comfort. No increase in occupant complaints
196 | 6.Report3 | Operation and maintenance | 2-Opt | Long Text | The building engineer at the location studied in this project stated during a telephone interview that the software provider contacted him on numerous occasions to inform him when supply air or return air temperatures exceeded their normal operating conditions. These remote observations allowed the building engineer to quickly assess and fix issues with his HVAC systems. Additionally, the building engineer noted that the provider was very responsive when he called them to report any hot calls in the building.