## Main
Automated Shading and Daylight Dimming - Site Savings Estimator
Chicago Climate
Use this worksheet to estimate the range of whole building lighting, HVAC and site energy savings from automated shading and dimming.
This estimator is intended to support site screening. It is NOT intended for incentive calculation or M&V.
See notes below for key assumptions and limitations. See cell comments for additional guidance.
Input cells shaded blue
Step 1: Calculate annual lighting energy savings
Orientation | Impacted Area (sf) | Dimming zone | Lighting Power Density (W/sf) | Annual "occupied mode" hours | Lighting kWh Impacted baseline | Lighting % savings (avg) | Lighting % savings (low) | Lighting % savings (high) | Lighting kWh savings (avg) | Lighting kWh savings (low) | Lighting kWh savings (high)
N | 20000 | 25' three rows dim | 1 | 3120 | 62400 | 49.23% | 42.23% | 58.23% | 30720 | 26352 | 36336
NE | 0 |  | 0 | 3120 | 0 | 0% | 0% | 0% | 0 | 0 | 0
E | 20000 | 25' three rows dim | 1 | 3120 | 62400 | 43.85% | 37.85% | 50.85% | 27360 | 23616 | 31728
SE | 0 |  | 0 | 3120 | 0 | 0% | 0% | 0% | 0 | 0 | 0
S | 20000 | 25' three rows dim | 1 | 3120 | 62400 | 40% | 32% | 48% | 24960 | 19968 | 29952
SW | 0 |  | 0 | 3120 | 0 | 0% | 0% | 0% | 0 | 0 | 0
W | 20000 | 25' three rows dim | 1 | 3120 | 62400 | 43.85% | 37.85% | 50.85% | 27360 | 23616 | 31728
NW | 0 |  | 0 | 3120 | 0 | 0% | 0% | 0% | 0 | 0 | 0
Total | 80000 |  |  |  | 249600 |  |  |  | 110400 | 93552 | 129744
Step 2: Calculate annual HVAC energy savings
Metric | Average | Low | High
Annual lighting energy savings | 110400 | 93552 | 129744
HVAC elec factor (kWh change/kWh lighting saved) | 0.14 | 0.14 | 0.14
HVAC gas factor (kWh change/kWh lighting saved) | -0.3 | -0.3 | -0.3
Annual elec energy savings (kWh) | 15456 | 13097.28 | 18164.16
Annual gas energy savings (kWh) | -33120 | -28065.6 | -38923.2
Step 3: Calculate annual site energy savings
Metric | Average | Low | High
Annual electricity use (kWh) | 800000 | 800000 | 800000
Annual gas use (kWh) | 200000 | 200000 | 200000
Annual site energy (kWh) | 1000000 | 1000000 | 1000000
Annual site energy savings | 92736 | 78583.68 | 108984.96
Site energy savings % | 9.274% | 7.858% | 10.9%
Assumptions and limitations
1. See the "Factors" tab for lighting and HVAC savings factors and assumptions
2. Lighting savings is solely from dimming and includes institutional tuning. Tuning baseline assumptions can be modified on "Factiors" tab.
3. HVAC savings are based on DOE prototype models. Be sure to review system type and associated fuel source assumptions
4. Savings factors are for Chicago climate, using TMY data.
5. Savings factors for other locations may be calculated using the methodology documented in the technical report.
Note on B12: Perimeter floor area impacted by the system.
Note on C12: 15' daylight zone can be modeled by selecting 25' two rows dim. But impacted area should include 25' perimeter depth
Note on D12: LPD with all lights on without dimming. If retrofit includes lamp/ballast upgrade, use post-retrofit LPD. (This estimator is solely for dimming and tuning savings)
Note on E12: Hours that lights are scheduled to be on. i.e. normal occupancy hours.
Note on A28: See "Factors" tab for assumptions for different building types
Note on A29: See "Factors" tab for assumptions for different building types
Note on A37: From utility bills
Note on A38: From utility bills

## Factors
Savings Factors - Chicago Climate
Lighting savings factors - without tuning savings
Data are based on FLEXLAB measured savings
Orientation | 25' two rows dim |  |  | 25' three rows dim |  |  | 25' two rows dim | 25' three rows dim
| Avg | Low | High | Avg | Low | High
N | 31% | 25% | 39% | 34% | 27% | 43%
NE | 27.5% | 22% | 34.5% | 30.5% | 24% | 38.5%
E | 24% | 19% | 30% | 27% | 21% | 34%
SE | 21.5% | 15.5% | 28% | 24.5% | 17.5% | 32%
S | 19% | 12% | 26% | 22% | 14% | 30%
SW | 21.5% | 15.5% | 28% | 24.5% | 17.5% | 32%
W | 24% | 19% | 30% | 27% | 21% | 34%
NW | 27.5% | 22% | 34.5% | 30.5% | 24% | 38.5%
Lighting savings factors - with tuning savings
Data are derived from the savings factors without tuning (above) and tuning baseline assumption, which can be adjusted.
Untuned basline (as % of tuned baseline) | 130%
Orientation | 25' two rows dim |  |  | 25' three rows dim
| Avg | Low | High | Avg | Low | High
N | 46.92% | 40.92% | 54.92% | 49.23% | 42.23% | 58.23%
NE | 44.23% | 38.73% | 51.23% | 46.54% | 40.04% | 54.54%
E | 41.54% | 36.54% | 47.54% | 43.85% | 37.85% | 50.85%
SE | 39.62% | 33.62% | 46.12% | 41.92% | 34.92% | 49.42%
S | 37.69% | 30.69% | 44.69% | 40% | 32% | 48%
SW | 39.62% | 33.62% | 46.12% | 41.92% | 34.92% | 49.42%
W | 41.54% | 36.54% | 47.54% | 43.85% | 37.85% | 50.85%
NW | 44.23% | 38.73% | 51.23% | 46.54% | 40.04% | 54.54%
HVAC factors
Data are derived from Energyplus simulations of the DOE prototype models
Building Prototype | HVAC energy factor (kWh change/kWh lighting saved) |  | System Type
| Electricity | Gas
Large Office | 0.14 | -0.3 | Central electric chiller and gas boiler. Hot water reheat.
Medium Office | 0.01 | -0.13 | Packaged units with electric reheat.
Primary School | 0.14 | -0.04 | Packaged units with gas heating.
Secondary School | 0.2 | -0.11 | Air cooled chillers and packaged units with gas heating.